RE: 		PLAN REVIEW COMMENTS – JOHN GRACE ARMS DEVELOPMENT

DATE: 		5/19/2025

PROJECT: 	JOHN GRACE ARMS DEVELOPMENT

21030 INDIAN ST

SOUTHFIELD, MI 48033

PROJECT#: 	PB25-0031

Angelo Bateast,

In follow up with the comments provided from the John Grace Arms development plan review from 4/29/2025, please see correction responses below.

ELECTRICAL

1.Provide Fault Current from DTE on the Transformers.

Response: Once received from DTE the Fault Current will be shared. DTE has been provided the design information to start service design but has not been completed as of yet.

2.Provide AIC Rating for the 125 Amp Electrical Panels in each residence.

Response: The project manual has the electrical panel AIC rating at 22k.

3. Provide Electrical Permit for the Cabling from ACCU to the FC provided by the Mechanical

Contractor, and the Mechanical.

Response: Comment will be communicated to the general contractor for electrician when project is awarded to have electrical permit pulled for cabling from ACCU to FC.

4. All lighting must meet the Energy Code of 2015.

Response: All lighting will meet the 2015 energy code upon submittal review.

5.Subject to field Inspection.

Response: Comment will be relayed to general contractor for subject to field inspection.

6. Electrical Contractor to meet the Electrical Inspector for rough, and final

inspections.

Response: Comment will be relayed to general contractor for subject for electrical rough and final inspections.

7. Provide a 1 inch conduit for the 2 #2 and #8 instead of a 3/4 inch conduit.

Response: Upsizing conduit to 1” as required.

MECHANICAL

- Limited information provided with submittal. Only sheets starting with M-(mechanical) and P- (plumbing) drawings were provided with submittal. No fire suppression or fire protection drawings provided or reviewed. Additional drawings/review may reveal new comments 107.1

Response: Fire suppression and fire alarm scope are a design build process and will be submitted once sub-contractors are awarded to the project. Provisions for fire suppression lead is shown along with dedicated location for backflow assembly. Based on flow test performed a fire pump will not be needed. Project manual includes specifications for fire suppression and fire alarm materials and install.

- Drawings show kitchen room # 141. Provide details on this kitchen to meet mechanical code requirements. 107.1. No mechanical equipment, hoods, fire suppression or gas piping drawings provided. It is the design professional s responsibility to design a code compliant system. Simple statements of code sections or statement to refer to architect do not show code compliance.

Response: Updated sheets M-101 and M-405 to rename kitchen as community space II. Will not be used for any food preparation.

- Exit access corridors require negative pressure. Provide details. 107.1

Response: Revised ventilation in corridors to provide negative pressure, refer to sheets M-401, M-405, M-406, M-407, and M-603,

- Show compliance with the International Energy Conservation Code (Comcheck would suffice) 301.2

Response: Comcheck for project completed to 2021 IECC standards, listed project title on M-001 under mechanical general notes #5.

- Where equipment or appliances requiring access are located on an elevated structure or the roof of a building so that personnel will have to climb higher than 16 feet above grade to access this equipment or appliances, an interior or exterior means of access shall be provided. Provide/show access to rooftop equipment per 306.5

Response: Roof hatch is shown on roof plans of existing building and addition, made call out on M-105 and M-106 to location of roof hatches.

- Condensate drainage required to meet section 307. Not enough information supplied in limited submission.

Response: Added detail E6 on M-505 to include requirements for condensate drains to meet section 307.

- Dryer exhaust required to meet section 504. Not enough information supplied in limited submission. Provide details and exhaust piping calculations for multiple dryers into single exhaust duct. Show how dryer exhausts are protected.

Response: Dryer ventilation exhaust revised to reflect a dedicated single ventilation for each dryer see revised layout on sheets M-105 and M-402.

- Any/all fire protection measures required shall be provided on drawings. The limited information provided does not spell out all fire blocking/protection measures required. Details conflict and show fire/smoke dampers in ducts, yet also show unprotected transfer grilles. Provide detailed schematic/isometric of ALL fire damper/smoke damper/fire and smoke damper locations and specify the dampers to be used. It is the design professional s responsibility to design a code compliant system. Simple statements of code sections or statement to refer to architect do not show code compliance 107.1, 302.2, 607, 607.2

Response: Added detail for fire and smoke dampers to spell out fire blocking required to comply with stated code compliance, see detail G1 on M-504.

- Provide fire dampers where ducts penetrate fire partitions separating the tenant spaces 607.5.3

Response: Coordinated wall sections from architectural drawings to ensure all fire rated assemblies had appropriate fire smoke dampers changes made on sheets M-101, M-401, M-403, and M-406.

- This plan review is not intended to identify all mechanical details that may have been omitted from the drawings or are inadequately or improperly shown. It may also identify items shown or not shown that the Mechanical Official wants to draw attention to. This review is based upon and limited to the available information provided and/or presented in the submittal only. Details and/or information not presented on the submitted drawings or contained in the

PLUMBING

- Limited information provided with submittal. Drawings referred to in P-sheets (plumbing) drawings, including but not limited to Architectural plans, roof plans, reflected ceiling plans, civil drawings were not provided with submittal and information thereon has not been reviewed. Upon review of these needed drawings and occupancy information, additional review comments may be noted 110.1

Response: Architect to coordinate full drawing submission set if required.

- Detail H-8 on sheet P-410 shows a kitchen. Please provide details for this kitchen to determine plumbing facilities required 110.1.

Response: Updated sheets P-101 & P-410 to rename kitchen as community space II. Will not be used for any food preparation.

- Sheet P-100; Provide documentation that existing/replacement sump can be connected to building sanitary, not storm 110.1.

Response: Provided note on sheets P-403 that existing elevator sump pump and sub-basement was not safely accessible during the time of design. Intent is to replace existing sump pumps with equivalent sizing and tie into closest adequate sanitary piping. Will review further when have ability to safely access sub-basement.

- Provide details on elevator drain tile sub soil system and elevator sump pits per 110.1.

Response: Provided note on sheets P-403 to provide information that existing elevator sump pump and sub-basement was not safely accessible during the time of design. Intent is to replace existing sump pumps with equivalent and tie into existing piping. Will review further when have ability to safely access sub-basement.

- Water supply system sizing conflicts and is inconsistent throughout the drawings. Provide consistent sizing details throughout 110.1. Provide water usage calculations to show water supply sizing.

Response: Revisions to sheet P-701 have been updated to reflect correct size piping for domestic water distribution.

- Any/all fire protection measures required shall be provided. The limited information provided does not spell out all fire blocking/protection measures required 110.1. Detail E-13 not sufficient.

Response: Added detail for pipe passing through fire rated wall assembly to show UL rated fire blocking. Refer to detail A8 on sheet P-501.

- Condensate drainage and traps required to meet 314.2.3, 314.2.3.1, 314.2.3.3, 314.2.4,

314.2.4.1, 314.2.5. Provide details.

Response: Condensate drain dimensions and piping verified to meet current code requirements found in table in detail G9 on sheet P-503.

- Detail H-8 on sheet P-410 reflects toilet room off kitchen, which is prohibited per 403.3.1, 403.3.2

Response: Updated sheets P-101 & P-410 to rename kitchen as community space II. Will not be used for any food preparation.

- Sheet P-601 backflow schedule is incomplete. Provide details on all backflow protection per 608, chapter 8, 110.1

Response: Updated sheet P-601 to include populated backflow schedule.

- Sanitary/Venting as drawn. Dry vents prohibited per 905.

Response: See revised venting drawing on P-701, removed all combination wet and dry vents as required.

- Detail A-8-Open ended drain Wye fitting is prohibited and must be a sanitary T per 909.2.

Response: See revised detail A8 on sheet P-501, connects wye fitting to sanitary line.

- Trap seal protection required (existing floor drains) and not detailed per 1002.4.1

Response: Updated detail A13 on sheet P-501 with note to include a waterless trap seal protection system for all existing floor drains. Provided manufacturer model number for reference.

- 13.Elevator specifications not provided with limited submittal. Oil interceptors may be required per 1003.4. Provide details and details on sump.

Response: Elevator style to be traction style and does not contain oil, thus will not require an oil interceptor. Refer to architectural drawings for elevator specifications.

- Provide all roof drainage calculations per 1106, provide isometrics 110.1

Response: Table with roof drainage calculations have been added to sheets P-301 and P-301. All roof drainage on addition is a gutter system that has been called out on sheet P-302. The existing building will replace existing roof conductors with new and the same sizes, however the existing configuration and sizing at the time of design cannot be safely verified.

- Sheet P-302 Addition roof plumbing plan does not show any roof drainage. Provide Roof drains per Chapter 11

Response: Roof drainage for addition is a gutter system and is now called out on sheet P-302. Refer to architectural drawings for gutter installation details and specifications.